| Switching Order No: |  |
| --- | --- |
| Isolated Work Area: | Station 5 Powerhouse Emergency Generator |
| Reason: | This procedure ISOLATES the Emergency Generator for Service |
| Notes: | The Emergency Generator (EG) is tested every Wednesday. 120V service to EG from panel E-PP1. 480 V feed from EG to switchgear. See last page. |

| Step No. | Operation | Time Operation Completed/ Operator Initials |
| --- | --- | --- |
|  | NOTIFY Hydro Control Center (HCC) that the Emergency Generator at Station 5 will be taken out of service and ISOLATED. |  |
| On the Operating Floor: |
|  | CONFIRM Breakers 52-1, 52-2, 52-G and 52-T are RACKED-IN to the CONNECT position. NOTE: Auto Transfer Switch from Essential to Non-Essential buses or vice versa will not operate with any of 52-1, 52-2, 52-T or 52-G Breakers RACKED - OUT. Transfer between the Essential to Non-Essential buses has to be performed manually. |  |
|  | USE the Generator Key (kept in a document holder located on a pillar to the left of 480V switchgear) to open the Emergency Generator compartment. |  |
| At the Emergency Generator, outside the Station 5 Powerhouse: |
|  | TURN the Generator Key Operated AUTO/OFF/MAN switch from the AUTO or MANUAL position to the OFF Position and BLOCK. |  |
|  | CLOSE and HOLD the main natural gas Shutoff Valve for the Emergency Generator. |  |
|  | OPEN and HOLD the Main 480VAC Output Breaker (inside the generator panel). |  |
| At the 480 V Switchgear on the Operating Floor: |
|  | TURN the Dev 43 Transfer Mode Auto/Manual Automatic Transfer Mode Selector switch from the Auto position to Manual position and BLOCK. NOTE: Automatic transfer via 52-T between the Essential and Non-essential bus will not occur when Dev 43 Transfer Mode Auto/Manual Automatic Transfer Mode Selector switch is in the MANUAL position. |  |
|  | CONFIRM the 52-G Emergency Generator F5B 800A Trip cell breaker is OPEN via illumination of the green indicator light, display of green semaphore flag, and by viewing the automatic transfer control screen. |  |
|  | RACK-OUT the F5B STANDBY EMERGENCY GENERATOR BREAKER and HOLD. NOTE: Auto Transfer Switch from Essential to Non-Essential buses or vice versa will not operate with any of 52-1, 52-2, 52-T or 52-G Breakers RACKED - OUT. Transfer between the Essential to Non-Essential buses has to be performed manually. |  |
| On the Operating Floor: |
|  | At Service Panel E-PP1, OPEN and HOLD Circuit Breakers 11 and 13. |  |
|  | Notify HCC that the Emergency Generator has been ISOLATED. |  |
|  | Fossil/Hydro Operations is now ready to receive mark-ups |  |
| CONTINUE WHEN ALL MARK-UPS ARE REMOVED AND WHEN READY TO RESTORE Emergency Generator |
| On the Operating Floor: |
|  | At Service Panel E-PP1, REMOVE HOLD and CLOSE Circuit Breakers 11 and 13. |  |
| At the Emergency Generator, outside the Station 5 Powerhouse: |
|  | CONFIRM Breakers 52-1 and 52-2 are CLOSED. |  |
|  | REMOVE HOLD and RACK-IN the F5B STANDBY EMERGENCY GENERATOR BREAKER 52-G. |  |
|  | REMOVE HOLD and CLOSE the Main 480VAC Output Breaker (inside the generator panel). |  |
|  | REMOVE HOLD and OPEN the main natural gas SHUTOFF VALVE for the STANDBY EMERGENCY GENERATOR. |  |
|  | REMOVE BLOCK and TURN Generator Key Operated AUTO/OFF/MAN switch to the AUTO Position. |  |
|  | RETURN Generator Key to documentation packet. |  |
|  | REMOVE BLOCK and TURN the 43 Transfer Mode Auto/Manual Automatic Transfer Mode Selector switch to AUTO. |  |
| On the Operating Floor: |
|  | NOTIFY HCC that the STANDBY EMERGENCY GENERATOR at Station 5 is back in service. |  |

| Out of Service |
| --- |
| Date | Time | Holding Authority | Performed By |

Figure 1 –Operating Floor

# Text boxes

480 V Switchgear

Emergency Generator

and Main 480 VAC output breaker

(outside)

E-PP1

Unit 1

Unit 2

Unit 3

Semaphore flag: green when open, red when closed